Page 2:

- On W2: put the cable 2 of the alternator

- On U2: put the cable 10 of the alternator

- On V2: put the cable 6 of the alternator

- On N2: put the cable 12 and 4 of the alternator

- On W1: put the cable 5 of the alternator

- On U1: put the cable 3 of the alternator

- On V1: put the cable 1 of the alternator

- On N1: put the cable 9 of the alternator

5) Take a switch type C315 TANDEM, move the fixing “patte” situating at the 2nd original mark of the longest switch, et move it on the original switch 8th mark.

Tight all the screw BTR of the switch at 12.5NM and put some red stop glue MESPOULET.

Glue the location small board for the borne REF: 2157 on the superior part of the switch

Page 3:

Link the switch with the beam REF: ATLASFAIS.QAS338GN like:

- The 6th cable of the beam on the 6th pale of the switch

- The 10th cable of the beam on the 10th pale of the switch

- The 5th cable of the beam on the 5th pale of the switch

- The 4th cable of the beam on the 12/4th pale of the switch with the “cosse” 4 of the cable 4/8

- The 9th cable of the beam on the 9th pale of the switch

- The 3rd cable of the beam on the 3rd pale of the switch

- The 2nd cable of the beam on the 6nd pale of the switch

- The 1st cable of the beam on the 1st pale of the switch

Maintain the cables “cosse ” of the switch with the bolting given with the switch like the next drawing.

6) When the switch is cabled, immobilize it and his breastplate (the moving red button toward the top) on the raising reference: ATLAS6600. Immobilize the total with 4 mechanic screws with cylindrical heads cracked of 5x60 for the part with the breastplate, 4 mechanical screws with cylindrical heads cracked of 5x45 for the other part, dish slide of 5 and brake screw nut of 5mm.

Page 4:

Tight at 2 Nm and verify when you tight that the breastplate pushing button is working correctly, and make a sign on the brake screw nuts. Put the silvery breastplate number on the top face of the breastplate and the grip ball on the bottom and tight the central screw.

7) Put in place the revamp with the switch on the alternator the switch breastplate disc side, and immobilize with the original screws, tight normally.

8) Put the remaining alternator cables in place on the switch like:

- the 7th cable on the 7th plate of the switch

- the 11th cable on the 11th plate of the switch

- the 8th cable on the 8th plate of the switch with the 8th  “cosse” of the cable 8/4 allready assemble in the chapter 5. Immobilize the “cosse” on the switch “pattes” like it’s written in the chapter 5.

9) Put the switch cables on the

- the 10th cable “cosse” of the switch  on the plate U2 of the 1st pale

- the 2nd  cable “cosse” of the switch  on the plate W2 of the 1st pale

- the 6th   cable “cosse” of the switch  on the plate V2 of the 1st pale

- the 3rd cable “cosse” of the switch  on the plate N2 of the 1st pale

Immobilize with 1 flat brass disc of 16mm, and 1 screw nut of 16mm in brass