The Katolight models D250f*j4 through the D415f*j4and the XSD245FRJ5 through the XSD336FRJ5 have been difficult to prime for some Technicians. Here is the recommended way to prime these engines.

- Prime the system to the engine from the remote tank if there is one if it is a base mounted tank you may skip this step.

- Plug or pinch off the return fuel line do this in a way that does not damage the fuel line or any fittings.

- Switch the unit to manual and allow it to crank over, this will build pressure in the fuel rail. When the pressure in the fuel rail gets above 60 PSI the air trapped in the system will be forced out through the injectors and the engine will fire. This may take 3 or 4 crank cycles. (30 or 40 seconds of total crank time)

- Once the air is mostly gone the engine will fire and run, shut the engine off as soon as the engine runs smooth.

- Restore the engine to its proper operating condition.

- The whole process should take under 5 min.