Procedure to field install a engine cool down timer in a control panel.

Install relay provided in the control panel 

Remove wires (8) and (25) from TB1 

Attach wire(s) #(8) to terminal 3 on the KD1 (relay)

Attach wire(s) #(25) to terminal 1 on the KD1 

Bring battery +  (wire # 48 on the TB1) to the KD1 terminal 2

Bring ground  (wire # 9 on the TB1) to the KD1 terminal 7

Run wires from 5 and 6 on the KD1 to E and E on TB1

Set the timer for what time the customer requests recommend 5 min  

