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PRODUCT COM #512


October 25, 2004


TO:
Generator Marketing, Generator Representatives, Generator Application Engineering, Warranty Service


FROM:
John Hamilton

SUBJECT:
430 MAGNAPLUS Link Board 

The standard link board for the 430 MAGNAPLUS is temporarily not available.  During the two to three weeks until the standard link board is again available, it will be replaced by an assembled link board as shown in the picture below.  This link board due to space limitations will have only 8 posts.  The generator will be shipped connected for 480 volt wye as shown below.  With this 8-point link board you will still be able to make all the desired connections.
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To reconnect for low wye reconnect the leads as shown below:
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Connect 1 and 7, 2 and 8, 3 and 9, 4, 5, 6 and 10, 11, 12 with links.

To reconnect for 120/240 volt single phase zigzag, connect as follows.  120 volts between L1 and N and between L2 and N.  240 volts between L1 and L2.
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