KATOLIGHT WINDING INFORMATION

KL SERIES PTO GENERATORS

SINGLE PHASE MODELS

MODEL
EXCITER RESISTANCE
GENERATOR RESISTANCE
EXCITER NO LOAD VOLTAGE


STATOR
ROTOR
STATOR
ROTOR
VDC

KLSI-25
23.5
.120
.0695
.750
11.8

KLM1-40
23.5
.120
.0695
.750
11.8

KLM1-50
23.5
.120
.0695
.750
11.8

KLM1-60
23.5
.120
.0695
.750
11.8

KLM1-75
23.5
.120
.0191
1.20
17.O

KLM1-100
23.5
.120
.0191
1.20
17.0

THREE PHASE MODELS

MODEL
EXCITER RESISTANCE
GENERATOR RESISTANCE
EXCITER NO LOAD VOLTAGE


STATOR
ROTOR
STATOR
ROTOR
VDC

KLM3-45
23.5
.120
.381
.750
11.8

KLM3-55
23.5
.120
.264
.810
12.5

KLM3-65
23.5
.120
.181
.990
14.1

KLM3-85
23.5
.120
.138
1.05
12.2

KLM3-105
23.5
.120
.138
1.05
12.2

KLM3-135
23.5
.120
.0692
1.37
12.2

