Olympian Retrofit Notes
· Record engine hours from old panel

· Record flywheel teeth, if applicable

· Analog Inputs are metric values, KPA and Celsius.   Use map#2 oil psi, map#4 coolant temp

· Remember to tie all analog(-) to battery(–) per drawing

· Typical CAT oil psi setpoints, 35psi/242kpa-warning, 30psi/207kpa-shutdown

· Typical CAT coolant temp. setpoints, 212F/100C-warning, 225F/108C shutdown

· Low coolant temp 70F/21C.  Setpoint is in the coolant temp analog input

· Second MPU may have to be added if genset only has one

· Bring wire, loom and connectors for any additional wiring needs

· Disable service maintenance interval

· Check event response configuration

· Disable generator reverse reactive power or set values at max 20% to prevent nuisance alarms.  

· Download configuration file and product status report upon completion

· If you are leaving the EIM module in place remember to read attached EIM document for wiring safety relay wire 5B through N/C E-Stop contacts.
· Wire 19 is the B+ flash circuit for the engine alternator, wire through a run relay for operation. 

· Cycle power to control panel upon completion of programming as we have seen some of the parameters not take until this has been done. 
