## Slide 1
Welcome to MTU electronics informational meeting.
We will cover:
Explanation of calibrations and software.
How calibrations are made.
Connecting to the ECU
ECU input and outputs
Fault Logs
Recording Data
Upload and download from the server
SAM CF cards
CF card programming
MTU Electronics

## Slide 2
MTU Electronics

## Slide 3
The engine controller on an MTU series 2000 or 4000 could be:
MDEC
ADEC
DDEC
Diasys is a laptop based electronic tool that supports MDEC and ADEC controllers.
MTU Electronics

## Slide 4
The engine controller is required for operating the engine.
By using various sensors and other electronic components, it controls fuel delivery and timing.
This means that all speed and load conditions are run by the engine controller.
At the same time, the condition of all sensor wiring and components are monitored by the controller for correct function.
MTU Electronics

## Slide 5
What is a calibration?

## Slide 6
This is a 1D parameter.
These are a single value or simply an On / Off switch.
What is a calibration?

## Slide 7
This is a 2D parameter.
It is a simple table with 1 axis and one line of data.
This one is for coolant pressure alarm limit 1.
Limit 1 = Yellow Alarm
If the coolant pressure is below this limit, the Yellow alarm will activate.
What is a calibration?

## Slide 8
This is a 3D parameter.
It has 2 axis and table of data.
This is for Rail Pressure
Based on engine RPM and Engine Torque, this table tells the controller where to set the rail pressure.
What is a calibration?

## Slide 9
This is an example of software logic.
Software is written in code. It can only be accessed by a small group of people.
It is updated frequently for many reasons. New emissions requirements, change in some function, etc.
Logic tables like this instruct the computer how to use the calibration values.
Software documents can be several thousand pages long.
What is software?

## Slide 10
All engines are first calibrated to run well at the emissions testing conditions. This work is done on an engine dyno.
25C Air temp
Sea level
Warm Coolant
After the engine runs well under these conditions, the compensation calibrations are developed.
How is a calibration made?

## Slide 11
What is a compensation calibration?
This is an additional calibration used to allow the engine to run well at all environmental conditions outside the emissions test area. Some of these calibrations have to be developed on-site.
High Altitude
Cold or Hot coolant conditions.
How is a calibration made?

## Slide 12
Example of injection timing table for Cold Engine
Example of injection timing table for Normal operating temp engine
How is a calibration made?

## Slide 13
This is a list of calibration rules.
A rule is simply a combination of 1D, 2D and 3D parameters required to enable a certain engine option to operate.
You could call it a calibration package.
Examples would be HP rating,
Throttle control type
Pre-lube available
How is a calibration made?

## Slide 14
This is the rule for 270 fan clutch.
It lists the correct setting for every calibration required for the 270 fan clutch NON Emissions cal.
How is a calibration made?

## Slide 15
Diasys is the tool required to connect to MTU engine governors
You can use Diasys to:
Check for diagnostic codes
Read current speed and load conditions
Read fueling rate
Check engine history for previous diagnostic codes
Run diagnostic tests on the engine
Make necessary calibration changes
Basic information about Diasys

## Slide 16: Diasys Operation and Functions
Getting Started

## Slide 17
Getting Started

## Slide 18
Standard warning appears when starting the software.
Dangers of making unauthorized changes
Protect your personal Diasys key (dongle).
Engine Operation Warning
Getting Started

## Slide 19
Getting Started
Two Options Available to Trained Field Personnel:
Customer
  Few Options or Functionality
Product Support
  Most options and Functionality available to Field Personnel
  Most common selection for field diagnostics and adjustments

## Slide 20
Select the controller you want to connect with.
Options in this screen will vary depending on the users training level. More options are available as training courses are completed.

## Slide 21
If you are not sure what controller you are working with, select a picture to view.

## Slide 22: Three Options Used Most in the Field
Entering a new engine on YOUR computer
Transferring engine data (calibrations) to-and-from the ‘Mainframe’
Open an engine description previously connected to

## Slide 23: Preparing to connect to the ECU
Name of Project or Unit which you working on
Name can be anything to help you remember the project
  Click on “New” to enter engine number

## Slide 24: Preparing to connect to the ECU
More than one engine can be entered by clicking ‘New’ again.
Click ‘OK’ when engine(s) is entered
Click ‘Create’ when all engines are entered
Engine Number can be entered OR a simple digit. DiaSys will automatically correct when connecting to the governor.

## Slide 25
Connect to the ECU
Few options are available until a connection to the governor has been made.

## Slide 26
Connect to the ECU
Drop-down menu will show the units you specified in the folder.
Select unit number which you wish to connect to
As mentioned earlier, DiaSys will automatically correct any errors in your number selection
The Green box ‘Establish Online Connection” is critical as follows:
Box checked for connection / update of controller.
Box UNchecked for controller delete and reflash.
Clicking ‘OK’ will begin the connection process.
This process will take several minutes (less if connected to this engine previously)
Warnings and information pop-ups will appear during connection process
Click OK/Yes for all

## Slide 27
Diasys Error Log

## Slide 28
Download the current error log file
Export the log to an Excel spreadsheet to save/e-mail
Delete the log file after a repair
List of all ECU activity
List of ‘WHO’ changed ‘WHAT’, and ‘WHEN’
Diasys Error Log

## Slide 29
Diasys Error Log

## Slide 30
Open the statistical error log.

## Slide 31: DiaSys Injector Test

## Slide 32: DiaSys Injector Test

## Slide 33
Injector Test
This is used to test the fuel injectors while the engine is running.
Its best performed under load
Should be repeated at least twice
DiaSys Injector Test

## Slide 34
Injector Test
The test screen will tell you the limits in which the test can be performed.
Push Start Test and wait a few minutes.
It will display the contribution of each cylinder and if it is considered a problem or not.
DiaSys Injector Test

## Slide 35
Injector Test
If the Injector Test Evaluation cal is turned on, this data will be displayed in the results.
DiaSys Injector Test

## Slide 36
This is a manual evaluation sheet for an injector test.
It will show how the data is used to determine injector contribution.
DiaSys Injector Test

## Slide 37
Injector Replacement
(ADEC 7 ONLY)
This is used to reset the operating hours of the fuel injectors.
Injector function receives compensation based on hours to maintain emissions levels.
Must change data when injector is installed.
DiaSys Injector Test

## Slide 38
DiaSys Injector Test

## Slide 39: DiaSys Recordings

## Slide 40
List of ALL recordable parameters available
Parameters selected by the user which will be recorded
DiaSys Recordings

## Slide 41: DiaSys Recordings
Two similar screens will appear
The first will show the selected recorded data ‘Live’ in a list
The second will show the selected recorded data ‘Live’ on a graph
The parameters on the left are ALL parameters which are being recorded
The parameters which the user wants to view are moved to the right by the user
The parameters on the right are shown on the screen after clicking ‘Ok’

## Slide 42: DiaSys Recordings
Sampling time is the rate at which DiaSys will record the data to your computer.
The ‘Shortest sampling’ and ‘Sampling time’ should match
Shorter sampling times are preferred.
Long sampling times can result in ‘altered’ data
After clicking ‘Ok’ the recording has started

## Slide 43: DiaSys Recordings
After clicking ‘Stop recording’ the following screen appears
To save the data click on ‘Yes’
Choose your location to save it, name it and click Save

## Slide 44: DiaSys / Upload or Download files

## Slide 45: DiaSys / Upload or Download files

## Slide 46: DiaSys / Upload or Download files
Before downloading cals, Diasys will send any calibration data from your PC back to the server.

## Slide 47: DiaSys / Upload or Download files
This screen shows which engine serial numbers will be sent back.

## Slide 48: DiaSys / Upload or Download files How to control files that upload.

## Slide 49
If you delete the engines from this database, the cal will not be sent back to the mainframe.
This should only be done if you made temporary changes for test purposes.
DiaSys / Upload or Download files How to control files that upload.

## Slide 50: DiaSys / Upload or Download files
Enter engine #
Select Modernized or Nominal Data
Modernized data means the calibration has been updated on the server.
Nominal means the cal has been loaded into a ECU and reported back to the server.

## Slide 51: DiaSys Basics Recordings
Diasys will tell you if there is newer data available.
After selecting the cal you want, it will automatically be placed in the folder with this serial number.
DiaSys / Upload or Download files

## Slide 52: Diasys Advanced Information

## Slide 53
Diasys Functions
Special Parameters
This is used to:
Configure inputs
Configure outputs
Diagnostic trouble code response.

## Slide 54
Special Parameters
This is used to:
Configure inputs & Outputs
Diagnostic trouble code response.
Diasys Functions

## Slide 55
Diagnostic trouble code response.
Diasys Functions

## Slide 56
Select DTC
If Monitoring is turned off, this code will not set.
Diasys Functions

## Slide 57
Select DTC
If monitoring is on,
This will set the response to the code.
Choices:
No response
Warning only
Speed Limitation
Torque Limitation
Engine Shutdown
Diasys Functions

## Slide 58
Edit Input and Output settings
Configure Red and Yellow lights
Set up feedback circuits from ECM
Set up Binary inputs (Start/Stop, override, etc.)
Diasys Functions

## Slide 59
Edit Input and Output settings
Assign each output channel from ECM.
Active High or Low means circuit requires +24V to activate.
Diasys Functions

## Slide 60
Crash Recorder
The ADEC crash recorder is a circular memory system that monitors key parameters.
In the event of certain serious trouble codes, the data in memory is stored from before during and after the event for future use.
The file can be downloaded and sent to MTU.
Diasys Functions

## Slide 61
Diasys Functions

## Slide 62
MDEC or ADEC Load Profile Table
What is the load profile data?
How do I find it?
What can I do with it?
Diasys Functions

## Slide 63
MDEC Load Profile Table Download
Diasys Functions

## Slide 64
MDEC Load Profile Table Converted to Load Factor
Diasys Functions

## Slide 65
MDEC Load Profile Table Converted to a Chart
What can this be used for?
Some customers want to understand the operating conditions of their engine.
It can tell you if the engine may be over or under powered for its intended use.
Many maintenance contracts are tied to load factor. Most customers guess at this number.
It may reveal opportunities for cost savings. This engine has over 5000 hours of idle time. A 20V4000C22 uses about 4.2 Gal/Hr idling.
@ 4/Gal = Aprox $89,000 in fuel.
Diasys Functions

## Slide 66
Diasys Functions
How to record and analyze data with Diasys

## Slide 67
Diasys Functions

## Slide 68
Diasys Functions

## Slide 69
Diasys Functions

## Slide 70
Familiar screen
All parameters which were recorded are on the left
User chooses which parameters to view and moves them to the right
Diasys Functions

## Slide 71
Parameter Information
P- Is a Pressure Parameter
L1L-P Coolant = Alarm Limit 1 (Yellow alarm)
L2L-P Coolant = Alarm Limit 2 (Red Alarm)
AL – Alarm Parameter
Fail code – Current DTC’s
AI1 Rohwerte- Analog Input 1 Raw data
FIP Rohwerte – Frequency Input Raw Data
Diasys Functions

## Slide 72
Parameter Information
T- Is a Temperature Parameter
U1L-T Fuel = Alarm Limit 1
(Yellow alarm)
U2L-T Fuel = Alarm Limit 2
(Red Alarm)
It is critical to check all STOP inputs when investigating a NO Start.
The engine may crank but will not start with the Stop activated
Diasys Functions

## Slide 73
Torque limitation code.
This will show the full load capability of the engine.
If the engine cannot make full power due to smoke control or DTC issue, this will inform you.
NOTE: Code 1 = Normal operation.
Diasys Functions

## Slide 74
Choose your recording
They will have a .rms extension
Click ‘Open’
Diasys Functions

## Slide 75
Generator with long crank time.
Review of Diasys recording shows the high pressure pump is slow to build pressure.
Diasys Functions

## Slide 76
Same type Generator with short crank time.
Diasys recording shows that this engine is functioning correctly.
Diasys Functions

## Slide 77
2 Generators sharing the load.
Complaint:
1 engine cycles in and out of ½ engine.
Other 2 do not.
Diasys recording shows that these 2 engines are carrying different loads.
One is near threshold for ½ engine. Other is not.
Diasys Functions

## Slide 78
Diasys Functions
This engine had an issue with uncontrollable rail pressure.
It would set codes for high and low pressure conditions.
The parameter for coil resistance is for the pump control coil.
Approx. 2 Ohms are normal. This engine had 440 Ohms.
Loose connector.

## Slide 79
Diasys Functions
Example of normal resistance.

## Slide 80
Diasys Functions
Another Rail Pressure problem example.
Rail Pressure command is steady, actual pressure is uncontrollable.

## Slide 81
Diasys Functions
Complaint:
Generator has slow response to load.
NOTE: This is not full load condition.
See torque limitation code.
8 = Smoke control.
This is limiting fuel and slowing engine response.

## Slide 82
Diasys Functions
Complaint:
Low power on Generator
Full Load
RPM is low
Torque limitation code = 1 (good)
If all environmental conditions are OK, this engine may be low on power.
Injector, Airflow or EOL trim

## Slide 83
SAM Module Information
CCB Card
SAM Connectors
CAN Resistors
SAM Module
Compact Flash Card

## Slide 84
Using Diasys with SAM
CF Card Programming.
Field Data Handling.
SAM software level
SAM Module Information

## Slide 85
The first step in using Diasys to connect with a SAM unit is to locate the correct Diasys.dat file.
This file is unique to each SAM software release.
It tells Diasys what parameters are available to view and modify.
It will be located on the FTP server or each CF card.
SAM Module Information

## Slide 86
Find the Diasys.dat file for this SW set

## Slide 87
Select SAM

## Slide 88
Create a new description for this SAM

## Slide 89
Create a new description for this SAM

## Slide 90
Open the description for this SAM

## Slide 91
Read the assembly description for this SAM
This tells DiaSys what parameters are available to view and change

## Slide 92
Establish link

## Slide 93
Establish link

## Slide 94
Select Module to log into.

## Slide 95
Select Module to log into.

## Slide 96
Now you are ready to change / take data.

## Slide 97
Diasys Functions
SAM Module Information
Using Diasys with SAM
CF Card Programming.
Field Data Handling.
SAM software level

## Slide 98
Diasys Functions
SAM Module Information
When a SAM file is sent via email, most likely the file structure will not work on a CF card.
Certain files must be available on the root directory.

## Slide 99
The CF cards should be pre-formatted.
However if you have to format one, it must be formatted in FAT protocol.

## Slide 100
Cards should be pre-formatted.
However if you have to format one, it must be formatted in FAT protocol.

## Slide 101
FAT 32 formatting will not work.
Only FAT is OK.

## Slide 102
Files as received from MTU
The SAM must be able to see the files inside this folder.
WRONG !!!

## Slide 103
CORRECT EXAMPLE OF SAM CF CARD FILE STRUCTURE

## Slide 104
Diasys Functions
SAM Module Information
Using Diasys with SAM
CF Card Programming.
Field Data Handling.
SAM software level

## Slide 105
Diasys Functions
SAM Module Information
The SAM software has a new feature in most applications called “Field Data Handling”.
This SAM software will “read” the ADEC software, cals and engine hours upon first power-up and updates the information regularly.
This feature will allow the ADEC to be replaced with no MTU support.
If a new ADEC is installed, the SAM will program the software, cal and hour information.
However, if FDH is used, the ADEC will set a code 555 alarm and a Yellow light.

## Slide 106
Diasys Functions
SAM Module Information

## Slide 107
Diasys Functions
SAM Module Information
Due to this new feature, it is not longer possible to swap SAM modules between machines. The SAM will set a code for incorrect data between the SAM and ADEC.
The secondary issue with this feature is the SAM CF cards. The cards have not changed, but because they save specific information, are no longer easily interchangeable between machines.

## Slide 108
BEFORE installing in SAM
When the Life Data function is turned on, the SAM will create many new files when it is used for the first time.
These files store the ADEC serial number, software, cal and run time.

## Slide 109
When the Life Data function is turned on, the SAM will create many new files when it is used for the first time.
These files store the ADEC serial number, software, cal and run time.
AFTER installing in SAM

## Slide 110
Diasys Functions
SAM Module Information
Using Diasys with SAM
CF Card Programming.
Field Data Handling.
SAM software level

## Slide 111
To determine the SAM node number and software level, this can be found in the plant.txt file.
AFTER installing in SAM

## Slide 112
This is the software level in the plant.txt file.
It is 40012 level 20
AFTER installing in SAM

## Slide 113
Under the device heading, this will tell you the SAM device number.
AFTER installing in SAM

## Slide 114
At the bottom of the page, the BUS device name list will indicate the node number for each module.
This may be different for each SAM software application. Ex. Generator, Frac, Marine may have different nodes assigned. If you install a used SAM, this needs to be verified.
AFTER installing in SAM

## Slide 115
Thank You !