peaker services, inc.

engineered systems group





[image: image1.png]


8080 KENSINGTON COURT

BRIGHTON, MICHIGAN 48116-8591
[image: image2.png]



1
[image: image3.png]




19-Jun-06
Page    1





DPG-2201 Frequently Asked Questions

1. What voltage application can I use the DPG-2201 (12 or 24)?

The DPG-2201 can be used with 12 or 24 volts.

2. During installation as a replacement to a previous version Barber-Colman   controller, do I have to do any re-wiring?

The DPG-2201 is a direct replacement for most Barber-Colman controllers. You can use existing wires.

3. I am unable to change parameter number 1.

You have DPG-2201-001 and this parameter cannot be changed. You need to start on parameter number 2. If you have DPG-2201-002, parameter number 1 should change.

4. I need to set parameter number 2 at 3500. The display screen only shows 2 digits.

How do I set this?

When you push the INC and DEC buttons at the same time it will display the first 2 digits. When you release the buttons it will display the last 2 digits.

Pressed: 3.5

Released: 00

5. After following the installation process I started the engine and it went directly

into Overspeed. Why did this happen?

You may need to fine tune your adjustments. See page 32 in your user manual (Manual 36523) and follow the calibration process.

6. The engine is running at 1800 rpm, but it is hunting. How do I prevent this?

You will need to adjust parameter number 8 (overall gain). While the engine is running lower this parameter if it is hunting fast. Raise this parameter if it is hunting slow.

7. Does the DPG-2201 have remote speed adjust capabilities?

No, it does not. You will need a DPG-2223 if you require this feature.

8. I heard a lot of digital controllers have to be setup with a computer. Do you need a 

PC to setup this controller?

The DPG-2201 can be setup in your shop using a PC or a technician can set it up in the field without a PC.
248-437-4174 ( 800-622-4224 ( FAX 248-437-8280 ( WEB www.peaker.com  ( EMAIL kstone@peaker.com


_956490892.doc
[image: image1.png]






