peaker services, inc.

engineered systems group





[image: image1.png]


8080 KENSINGTON COURT

BRIGHTON, MICHIGAN 48116-8591
[image: image2.png]



1
[image: image3.png]




19-Jun-06
Page    1

DPG-2201 Troubleshooting
Overspeed-

You want the display screen to read a blinking 05. Use the Increase or Decrease button to adjust. When the display screen reads a blinking 05, press Select. The display screen should stop blinking. Use the Increase or Decrease button to adjust this parameter to 35. When the display screen reads 35 press Enter.

Start the Generator.

If the generator still goes into overspeed follow the next step. 

You want the display screen to read a blinking 02. Use the Increase or Decrease button to adjust. When the display screen reads a blinking 02, press Select. The display screen should stop blinking. Using the Decrease button change this parameter to 1000 RPM (if parameter 1 has not been set, change this to 2000 Hz). 

Increase & Decrease buttons pushed at the same time – 10 is displayed.

Buttons released – 00 is displayed.

When the display reads 1000 press Enter.
Start the Generator. Measure how may Hz your generator is producing. Gradually increase parameter number 2 by increments of 100 RPM to get your engine to run at 60 Hz. When your engine has reached 60 Hz press Enter.

Hunting-

You want the display screen to read a blinking 08. Use the Increase or Decrease button to adjust. When the display screen reads 08, press Select. The display screen should stop blinking. This is the Overall Gain Parameter for your Set Speed. (The engine needs to be running). If the engine is hunting fast decrease this parameter. If the engine is hunting slow increase this parameter. When the hunting has stopped press Enter.  
248-437-4174 ( 800-622-4224 ( FAX 248-437-8280 ( WEB www.peaker.com  ( EMAIL kstone@peaker.com


_956490892.doc
[image: image1.png]






